Use of geothermal energy and seawater for heating and cooling of the new terminal building in the airport of Thessaloniki.

Dimitrios Mendrinos  and Constantine Karytsas

Geothermal Department, Centre for Renewable Energy Sources, 19th Km Marathon Ave, 19009 Pikermi-Attica, Greece

# Abstract

A system of water source heat pumps using as a heat source both geothermal water of 42ºC and seawater of 15ºC during winter and 25ºC seawater as a heat sink during summer can cover 8 MWth and 16.800 MWhth heating and 7MWc cooling loads of the new terminal building of the airport “Makedonia” of Thessaloniki. The system will operate with a net seasonal performance factor (SPF) of 4,3 provided that a centralized energy management system and inverters regulate all pumps and fans. Energy costs amount at 0,015 €/kWh (annual operation and maintenance costs only), or at 0,028 €/kWh including the amortization of the equipment supplying energy to the building.

##### Keywords: Heat Pumps, Groundwater, Seawater, Heating, Cooling